DTL Cage Stuck Locked and Low Level RF Signal
October 24, 2012
V.T.

To be able to open the DTL cage a “low level RF” signal must be sent from the RF system to Safety.
The low level RF signal is the “AND” sum of eight “low level RF” signals, one for each tank inside the DTL cage. If any of the eight tanks is not sending the “low level RF” signal, the ASU does not release the DTL cage keys.

The box containing the electronics for the “low level RF” signals is located at the east end, outside the DTL cage – see picture below

Inside the box, on the PCB there is a row of LEDs. When a tank is at low level RF the corresponding LED is on. To release the DTL cage keys all LEDs must be on.

Next to the row of LEDs there is a row of relays in a metal can (circled in red in the picture below). If one LED is not lit when you expect it to be, remove the corresponding relay from its socket and re-install. If the LED is lit, you had an oxidized contact, if it doesn't you need to replace the relay. These relays are store items. Part #: .3-7/10047 type 712-5V (it's a 5 V relay). A fault report to RF System should be filed.